## Tabelle1
Registermapping Leonis3.5 app v4 and higher
User input registers map (IR0..99):
description | register address | range | function
REG_I_T | 0 |  | 0.1C. Temperature measured by device. (with self heating compensation)
REG_I_RH | 1 |  | 1%. Relative humidity measured by device. (with self heating compensation)
reserved | 2
REG_I_DIG_INS | 3 |  | digital inputs; Bit 0 → input 1 state, Bit1 → input 2 state
REG_I_TP | 4 |  | dew point temperature, signed 0.1°C
REG_I_AH | 5 |  | absolute humidity, 0.1 g/m^3
REG_I_CO2 | 6 |  | CO2, ppm; 32767 in case of CO2 sensor error
reserved | 7
reserved | 8
REG_I_V_0_10 | 9 |  | 0-10 Vin input, mV
reserved | 10..19
REG_I_HW_OK_BITS | 20 |  | Bit 0 → Touch Controller OK, Bit 1 → QSPIFlash OK, Bit 2 → Temperature Humidity Sensor OK, Bit 3 → EEPROM OK, Bit 4 → CO2 sensor OK, Bit 5 → 32 Khz crystal OK
REG_I_STRIP_RES_BITS | 21 |  | Bit 0 → ASM1, Bit 1 → ASM2, Bit 2 → ASM3, Bit 3 → ASM4 (for detection of assembly version)
REG_I_UID_high | 22 |  | unique serial microcontroller number high half
REG_I_UID_low | 23 |  | unique serial microcontroller number low half
reserved | 24
reserved | 25
reserved | 26..29
REG_I_UI_PERM_CONFIG_CRC | 30 |  | CRC of permanent HR registers of UI configuration. Used for identifying of UI config and it's correctness check. PLC/PC tool can check if configuration is uploaded correctly and stays untouched
HW_ID | 31 |  | hardware id
FW_ID | 32 |  | firmware version
FLASH_ID | 33 |  | flash file system version (icons sets can be distinguished by giving different version numbers)
RTC_SEC | 34 | 0-59 | RTC seconds
RTC_MIN | 35 | 0-59 | RTC minutes
RTC_HOUR | 36 | 0-23 | RTC hours
RTC_WEEKDAY | 37 | 1-7 | RTC week day (Monday = 1, Tuesday = 2, …)
RTC_DAY | 38 | 1-31 | RTC day
RTC_MON | 39 | 1-12 | RTC month
RTC_YEAR | 40 | 0-99 | RTC year
reserved | 41..43
REG_I_TOUCH_ACTIVE | 44
REG_I_TOUCH_X | 45
REG_I_TOUCH_Y | 46
reserved | 47
REG_I_T_SCD30 | 48 |  | 0.1C. Temperature measured by SCD30 sensor
REG_I_RH_SCD30 | 49 |  | 1%. Humidity measured by SCD30 sensor
reserved | 50..99
Auxilary input registers map (IR1000..1002):
description | register address | range | function
HW_ID | 1000 |  | hardware id
FW_ID | 1001 |  | firmware version
FLASH_ID | 1002 |  | flash file system version (icons sets can be distinguished by giving different version numbers)
User holding registers map (0..499, non-permanent registers):
description | register address | range | function
REG_H_USER_VAR1 | 0
… | …
REG_H_USER_VAR100_SCREEN | 99 |  | special user register, is used to hold current screen ID (0 - first, 1 - second … screen).
reserved | 100…149
REG_H_EN_CONFIG_WRITE | 150 |  | password for write access enable for configuration change
REG_H_BACKLIGHT_BRIGHTNESS | 151 |  | modbus backlight brightness control (0-100, low priority: written value active only until next key press)
reserved | 152
reserved | 153
REG_H_BACKLIGHT_ACTIVE | 154 |  | active brightness (100-1%)
REG_H_BACKLIGHT_STNDBY | 155 |  | standby brightness (20-0%)
REG_H_STANDBY_TIME_01S | 156 |  | standby brightness activation time (0.1 sec unit)
REG_H_U_OC_OUT_1 | 157 |  | 0-10000 mV out channel 1 (for 2x0-10Vout assembly version); 0/1 or 0..10000 (0.01% unit) for OC binary or OC PWM mode accordingly (for 2xOC assembly version)
REG_H_U_OC_OUT_2 | 158 |  | 0-10000 mV out channel 2 (for 2x0-10Vout assembly version); 0/1 or 0..10000 (0.01% unit) for OC binary or OC PWM mode accordingly (for 2xOC assembly version)
reserved | 159…169
REG_H_RTC_SET_SEC | 170 | 0-59 | RTC seconds set
REG_H_RTC_SET_MIN | 171 | 0-59 | RTC minutes set
REG_H_RTC_SET_HOUR | 172 | 0-23 | RTC hours set
REG_H_RTC_SET_DAY | 173 | 1-31 | RTC day set
REG_H_RTC_SET_MON | 174 | 1-12 | RTC month set
REG_H_RTC_SET_YEAR | 175 | 0-99 | RTC year set (to set RTC, all regs should be written in this order: seconds, minutes, hours, day, month, year )
reserved | 176…179
REG_H_SYSTEM_MENU_LOCK | 180 |  | System menu lock if HR180 > 0
reserved | 181…199
REG_H_TEXT1_1 .. REG_H_TEXT1_12 | 200 |  | 24 bytes(12 registers) for user string 1. Each register contains 2 characters, first at lower byte, second - at higher. So HR[200] = 0x3130 means that text will be "01".
REG_H_TEXT2_1 .. REG_H_TEXT2_12 | 212 |  | 24 bytes(12 registers) for user string 2
REG_H_TEXT3_1 .. REG_H_TEXT3_12 | 224 |  | 24 bytes(12 registers) for user string 3
REG_H_TEXT4_1 .. REG_H_TEXT4_12 | 236 |  | 24 bytes(12 registers) for user string 4
REG_H_TEXT5_1 .. REG_H_TEXT5_12 | 248 |  | 24 bytes(12 registers) for user string 5
REG_H_TEXT6_1 .. REG_H_TEXT6_12 | 260 |  | 24 bytes(12 registers) for user string 6
REG_H_TEXT7_1 .. REG_H_TEXT7_12 | 272 |  | 24 bytes(12 registers) for user string 7
REG_H_TEXT8_1 .. REG_H_TEXT8_12 | 284 |  | 24 bytes(12 registers) for user string 8
REG_H_TEXT9_1 .. REG_H_TEXT9_12 | 296 |  | 24 bytes(12 registers) for user string 9
REG_H_TEXT10_1 .. REG_H_TEXT10_12 | 308 |  | 24 bytes(12 registers) for user string 10
REG_H_TEXT11_1 .. REG_H_TEXT11_12 | 320 |  | 24 bytes(12 registers) for user string 11
REG_H_TEXT12_1 .. REG_H_TEXT12_12 | 332 |  | 24 bytes(12 registers) for user string 12
REG_H_TEXT13_1 .. REG_H_TEXT13_12 | 344 |  | 24 bytes(12 registers) for user string 13
REG_H_TEXT14_1 .. REG_H_TEXT14_12 | 356 |  | 24 bytes(12 registers) for user string 14
REG_H_TEXT15_1 .. REG_H_TEXT15_12 | 368 |  | 24 bytes(12 registers) for user string 15
REG_H_TEXT16_1 .. REG_H_TEXT16_12 | 380 |  | 24 bytes(12 registers) for user string 16
REG_H_TEXT17_1 .. REG_H_TEXT17_12 | 392 |  | 24 bytes(12 registers) for user string 17
REG_H_TEXT18_1 .. REG_H_TEXT18_12 | 404 |  | 24 bytes(12 registers) for user string 18
REG_H_TEXT19_1 .. REG_H_TEXT19_12 | 416 |  | 24 bytes(12 registers) for user string 19
REG_H_TEXT20_1 .. REG_H_TEXT20_12 | 428 |  | 24 bytes(12 registers) for user string 20
reserved | 440...449
IR0 mapped to HR | 450
… | …
IR49 mapped to HR | 499
Permanent register are stored in EEPROM for long life time (about 10 Mio cycles)