Works with hardware: fb2_6xS0

Latest software version: v0.1

(bootloader supported)

DipSwitch function:

DSW1..6 Address 1..63 
7 parity on (off) 
8 even parity (odd parity) 
9,10: 00 4800 
          10 9600 
           01 19200 
           11 38400 Bd

INPUT REGISTERS------------------------------------------------------------------------------------------------------------------

All input registers are also readable as input status bits.

IR0 = S0-1..S0-6 input processed as digital inputs; bit[0:6]

IR1 = internal 12V board voltage value used for S0, [0.1V]

IR2 = S0 input channel count; 2 or 6 (depends on assembly version)

IR3 = FRAM memory continuation code: 127(dec) - FRAM initialized successfully, 0 - FRAM initialization error

IR4 = Life counter 16bit; increase value by 1 each second

IR1000 = HW_ID = 1750

IR1001 = SW version

HOLDING REGISTERS--------------------------------------------------------------------------------------------------------------

Permanent registers:

HR0[15:0]-HR1[31:16] = S0-1 input 32bit counter

...

HR10[15:0]-HR11[31:16] = S0-6 input 32bit counter

DETAILS-------------------------------------------------------------------------------------------------------------------------------

At power software detects device assembly version: 2-channels or 6-channels. In case 2-channels version, values of permanent registers and IR0 input bits for ch4...ch6 are 0.

Standard S0 pulse period is 60ms (30ms low/30ms high). Software uses 15ms filtering time to improve stability against noise and pulse waveform deviations.